SECTION IX

STUDENT HANDOUTS

FIRE APPARATUS ENGINEER/PUMPING APPARATUS DRIVER/OPERATOR

STUDENT HANDOUTS

THEY MUST BE GIVEN TO THE STUDENT TO SUPPLEMENT PUBLISHED REFERENCED MATERIAL.

BASIC CONCEPTS, FORMULAS AND COURSE STANDARDS

For course, safety and testing purposes (written and practical), the Fire Apparatus Engineer Committee has accepted standard GPM and friction losses commonly used in the fire service.  Departments are encouraged to flow test their own hose, appliances and equipment to determine the actual friction loss.  The FAE Committee does, however, encourage the use of the following standard flows, friction loss factors,  formulas and general operating guidelines as being both safe and effective for fireground purposes.

WATER MEASUREMENTS

| 1 cubic foot of water weighs | 62.5 lbs. |
| --- | --- |
| 1 cubic foot of water contains | 1,728 cubic inches |
| 1 cubic foot of water contains | 7.5 gallons |
| 1 gallon of water weighs | 8.35 lbs. |
| 1 gallon of water contains | 231 cubic inches |

HEAD AND ATMOSPHERIC PRESSURE

1 foot of water exerts a back pressure of .434 psi.

Example:  When working from a standpipe at a point 100 feet above the street, the engineer must provide 43.4 psi to overcome the back pressure from the elevation.  In addition, he must provide pressure necessary to overcome friction loss and provide nozzle pressure.

1 psi will elevate water 2.304 feet.

Atmospheric pressure at sea level = 14.7 psi

Theoretically, maximum lift for drafting would be 34 feet.

This is determined by taking the atmospheric pressure, (14.7 psi) multiplied by the number of feet each psi lifts water (2.304 ft.) to give 33.87 or 34 feet.  Practically speaking, lifts of over 20 feet should not be attempted.

1” mercury (inches of vacuum) = 1.13 ft. of lift

ESTIMATING AVAILABLE WATER FROM A HYDRANT

A recommended minimum of 10 psi* should be maintained on the compound gauge when taking water from a hydrant.

*This varies from recommendations in IFSTA Pumping Apparatus, Driver/Operator Handbook, 1st edition..

The terms “static pressure” and “residual pressure” are familiar to every firefighter.  However, the difference between them is all too often not properly understood.  Static pressure, we say, is the pressure that exists on a given hydrant when no water is flowing.  This pressure is same pressure that is available at the water source.  Whether the source be a gravity tank or a pumping station is not important.

Once the hydrant is open and a flow of water is present, a drop in pressure will occur.  This drop in pressure is due to the friction loss that is now occurring in the water main system between the water source and the pump.  The larger the water main between the source of supply and the hydrant, the less friction loss.  The remaining pressure on the main is that which we term residual pressure.

Since we have friction loss on the suction side also, we again must consider the same factors as we considered on the discharge side.

The farther the pumper in use is from the hydrant, the less usable pressure due to increased friction loss.  The faster the water is moving (velocity), the greater the loss.  If the flow from the hydrant is doubled, the friction loss will be 4 times as great.

It is this last factor that will enable the pump operator to tell how many lines the available water pressure will enable him to handle.

Example:  If the intake compound gauge showed 70 psi before any lines are charged (static pressure), a 2½” line with a 250 GPM fog nozzle is then charged and the intake pressure drops to 67 psi.  This indicates that the friction loss between the source of supply and the pump intake is 3 psi with 250 GPM flowing.  By applying the factor - friction loss varies as the (flow)2 - it is a simple matter to calculate the number of lines of the same size the hydrant can supply.

| Line(2) | GPM | Calculation for psi loss |
| --- | --- | --- |
| 1 | 250 | = 3 |
| 2 | 500 | flow is twice the original - (2)2 = 4 x 3 psi drop = 12 |
| 3 | 750 | flow is triple the original - (3)2 = 9 x 3 psi drop = 27 |
| 4 | 1000 | flow is 4 times the original - (4)2 = 16 x 3 psi drop = 48 |
| 5 | 1250 | flow is 5 times the original - (5)2 = 25 x 3 psi drop = 75 (The pressure required for 5 lines is greater than available and cannot be supplied.) |

Thus by noting the static pressure reading and applying the numbers 4, 9, 16 or 25 to the pressure drop of the first line, a Fire Apparatus Engineer can determine how many more lines of the same flow he can supply.

As can be seen from the example, the Fire Apparatus Engineer could supply 3 additional or more 250 GPM lines for a total of 4 - 250 GPM lines with a residual pressure of approximately 22 psi.

ESTIMATING AVAILABLE WATER FROM HYDRANTS

In estimating available water, two things must be considered.

1.  Quality/quantity of the water supply system

2.  Fire department connections to the system

Although the following method can give inference to both, the primary concern is the water available for firefighting as the fire engineer has connected to the system.

The method employed used the Second Friction Loss Rule that states:

“In the same size hose, friction loss varies approximately as the square of the velocity of flow.”

Therefore if the velocity is doubled, friction loss is quadrupled.

To square a number, multiply the number times itself.

EXAMPLE 1:

| Velocity | Velocity | #1 | Total |
| --- | --- | --- | --- |
|  | Squared | Drop | Drop |
| Doubled = 2 | 4 | 3 psi | 12 psi |
| Quadrupled = 4 | 16 | 3 psi | 3 psi |
| Quintupled = 5 | 25 | 3 psi | 75 psi |

EXAMPLE 2:

| Velocity | Velocity | #1 | Total |
| --- | --- | --- | --- |
|  | Squared | Drop | Drop |
| Doubled = 2 | 4 | 6 psi | 24 psi |
| Tripled = 3 | 9 | 6 psi | 54 psi |
| Quadrupled = 4 | 16 | 6 psi | 96 psi |
| Quintupled = 5 | 25 | 6 psi | 150 psi |

To Estimate Water Available:

1.  Note static reading

2.  Note drop after discharging first line

3.  Multiply the drop from first line by the square of the velocity to see if `		the original flow may be doubled, tripled, etc.

Multiply by  4 if doubling flow

Multiply by  9 if tripling flow

Multiply by 16 if quadrupling flow

Multiply by 25 if quintupling flow

4.  Subtract total drop from original static pressure, but do not take 	Compound Gauge lower than 10 psi.

5.  Product from #3 and your original flow rate will determine total flow.

COMPONENTS OF A MOBILE WATER SUPPLY OPERATION

A.  Apparatus

1.  Tanker/tender

a.  NFPA minimum

1.  1000 gallon capacity

2.  750 GPM

b.  Construction Features

1.  tank capacity and size

2.  chassis and axle loading

3.  engine and drive train type and size

4.  dump and vent size

5.  pump location and size

6.  tank type or style

c.  Use

1.  combination

a.  attack

b.  supply

2.  shuttle

a.  dump considerations

- loading considerations

- additional considerations depending on local conditions

3.  Nurse (connected to pumper)

2.  Pumpers

a.  pump capacity

b.  hose carried

c.  fittings and adapters

d.  use

1.  pump at water source

2.  unload tankers (power unload or nurse)

3.  relay (open or closed)

4.  fire attack

B.  Portable Tanks

1.  Function

a.  reservoir

b.  dumping site for tanks

2.  Size

a.  500-6,000 gallons

b.  circular or square

3.  Construction

a.  folding synthetic

b.  floating collar

4.  Use

a.  position and spotting for dumping and drafting

b.  level surface

c.  access and turn around

C.  Auxiliary Equipment

1.  Portable Pumps

a.  Lightweight

1.  easily carried to water source

2.  minimum manpower required

b.  High volume at low pressure

2.  Loading and Unloading Dumps

a.  Special hoses or chutes

b.  Jet drafts

c.  Siphons or transfer devices

d.  Low level strainers

e.  Fill devices

f.  Cam-lock or quick connect couplings

#### PUMP TESTS

1.  Pre-Service Tests

- Certification Test

| 1 | 2 hour | 100% @ 150 psi |
| --- | --- | --- |
| 2 | ½ hour | 70% @ 200 psi |
| 3 | ½ hour | 50% @ 250 psi |
| 4 | 10 minutes | 100% @ 165 psi (overload or spurt test) |

2.  Service Test

| 20 minutes | 100% @ 150 psi |
| --- | --- |
| 10 minutes | 70% @ 200 psi |
| 10 minutes | 50% @ 250 psi |
| 100% @ 165 psi long enough to get readings (optional) (overload or spurt test) |

Pump Tests:  A minimum of 10 psi should be maintained on the compound gauge when taking water from a hydrant.

100% capacity @ 150 psi net pump pressure

70% capacity @ 200 psi net pump pressure

50% capacity @ 250 psi net pump pressure

COMPUTING NET ENGINE PRESSURE

1.  Net Engine Pressure (NEP) is the measurement of the total work performed by the pump:

a.  To lift water into the pump

b.  To discharge water from the pump

2.  Allowances are made for:

a.  Friction Loss in intake hose

b.  Height of lift

3.  Friction Loss Factors in Hard Suction Hose and Strainer (measured in psi):

| Rated | Diameter | For 10 feet of | For Each Additional |
| --- | --- | --- | --- |
| Capacity | Suction Hose | Suction Hose | 10 Feet of |
| Of Pumper | In inches |  | Suction Hose |
| 500 GPM | 4 | 6 | Plus 1 |
|  | 4½ | 3½ | Plus ½ |
| 750 GPM | 4½ | 7 | Plus 1½ |
|  | 5 | 4½ | Plus 1 |
| 1000 GPM | 4½ | 12 | Plus 2½ |
|  | 5 | 8 | Plus 1½ |
|  | 6 | 4 | Plus ½ |
| 1250 GPM | 5 | 12½ | Plus 2 |
|  | 6 | 6½ | Plus ½ |
| 1500 GPM | 6 | 9 | Plus 1 |
|  | 2-5 | 7 | Plus 1 |
|  | 2-6 | 2 | Plus ½ |
| 1750 GPM | 6 | 12½ | Plus 1½ |
|  | 2-5 | 6½ | Plus 1 |
|  | 2-6 | 3 | Plus ½ |
| 2000 GPM | 2-5 | 8 | Plus 1½ |
|  | 2-6 | 4 | Plus ½ |

COMPUTING NET ENGINE PRESSURE WHEN DRAFTING

N.E.P. = Suction Side Work + Discharge Side Work

1.  Work performed on the Discharge side of the pump is indicated on the pump’s discharge gauge.

2.  Work performed on the Suction side on the pump is determined by computing the following formula:

Work (psi) = Lift (Ft.) + Intake Hose F.L. (psi)

2.3 ft.

Steps:

a.  Determine the Lift (ft.)

b.  Determine the F.L. in the intake hose used

c.  Add Lift and F.L. together

d.  Divide by 2.3 (2.3 is the amount of lift (ft.) that 1 psi of water pressure will 	support)

Example

“A pumper is discharging 1000 GPM at a pressure of 142 psi.  The pumper is drafting water with a lift of 10 ft. through 20 ft. of 5” hard suction hose and strainer.  What is the NEP?

NEP = Suction Side Work + Discharge Side Work

S.S. Work   =   10 ft. + 9.5 psi    =    19.5 ft. psi     =   8.47 psi

2.3 ft.                     2.3 ft.

D.S. Work = 142 psi

NEP = 8.47 psi + 142 psi

NEP = 150 psi

DETERMINING THE PUMP DISCHARGE PRESSURES FOR THE SERVICE TEST

N.E.P. = Suction Side Work + Discharge Side Work

To determine the pump discharge pressures for a service test, the Suction Side Work must be subtracted from the NEP.

Pump Discharge Pressure (PDP) = NEP - Suction Side Work

Example

“A 1000 GPM pumper is to perform an Annual Service Test.  What are the desired readings on the pump discharge gauge for the following tests:

1.  100% capacity test @ 150 psi NEP

2.    70% capacity test @ 200 psi NEP

3.    50% capacity test @ 250 psi NEP

“The pumper is using 2-10 ft. sections for 5” hard suction hose.  The pump has been primed.  The Compound Gauge reading is approximately 10” Hg.”

Steps:

1.  Find the Lift.  10” Hg x 1.13 ft. = 11.3 ft.

2.  Find F.L. in the hard suction hose.  5” = 9.5 psi

3.  Compute Suction Side Work

S.S. Work  =  Lift + F.L.   =   11.3 ft. + 9.5 psi   =   20.8 ft. psi   = 9 psi

2.3 ft.                     2.3 ft.                  2.3 ft.

4.  Solve for Pump Discharge Pressure (PDP)

NEP		-	S.S. WORK	=	  PDP

#1	150 psi		-	     9 psi	=	141 psi

#2	200 psi		-	     9 psi	=	191 psi

#3	250 psi		-	     9 psi	=	241 psi

COMPUTING NET ENGINE PRESSURE  WHEN THE PUMP IS BEING SUPPLIED BY A POSITIVE PRESSURE WATER SOURCE (HYDRANT)

1.  No work is being performed on the suction side of the pump

2.  The incoming pressure added to the discharge pressure, produced by the 	pump, produces the total discharge pressure.

3.  NEP - the total work performed by the pump.  Therefore, the incoming pressure must be subtracted for the discharge pressure (found on the discharge pressure gauge) to find the NEP of the pump.

NEP = PUMP DISCHARGE PRESSURE (PDP) - INTAKE PRESSURE (IP)

Example

A pumper is being supplied by a hydrant.  The compound gauge shows a residual pressure of 25 psi.  The discharge pressure is 175 psi.  What is the NEP?

NEP    =      PDP     -       IP

=    175 psi   -    25 psi

=    150 psi

NOTES FOR VARIOUS NOZZLE PRESSURES ON FOG NOZZLES

GPM from fog nozzles at various pressure = rated GPM x    x .1

Examples:

250 GPM at 80 psi		120 GPM at 80 psi		120 GPM at 50 psi

x   9				x  9				x  7

2250                                      1080                                        840

x .1				x .1				 x.1

225.0 GPM                            108.0 GPM                              84.0 GPM

GPM’S from CIRCULAR OPENINGS

Computing GPM’s from circular openings shall use the following formula:

GPM’s = 29.7d2

D = diameter of orifice   P = flow pressure (psi) of discharging stream

HAND LINES/ MASTER STREAMS

FAE will consider all flows up to 350 GPM’s to be considered HAND LINES.  All flows over 350 GPM’s will be considered MASTER STREAMS.

Nozzle Pressures

Smooth Bore

Hand Held	=   50 psi

Master		=   80 psi

Fogs		(this includes fogs on master stream devices)

Most fogs	= 100 psi

NOZZLE REACTION

Newton’s Third Law of Motion:  “For every action there is an equal and opposite reaction.”  As water leaves a nozzle under pressure, it causes a reactionary force in the opposite direction.  The formula used for calculation of nozzle reaction is NR = 1.57D2P

For fog nozzles and master stream smooth  bore tips, fireground nozzle reaction calculations can be computed at approximately ½  the flow (measured in lbs.).

ANGLE OF DEFLECTION AND EFFECTIVE REACH

The reach of fire streams is affected by two variables:

1.  Air resistance

2.  Gravity

The air resistance increases at an accelerated rate as the pressure is raised with the same tip.

The greatest horizontal reach occurs at elevations of 30-34 degrees.

Maximum effective vertical reach of a fire stream occurs at 60-75 degrees.

The third floor may be said to be the highest floor to which streams may 	be thrown effectively from street level. (Casey, pg. 329)

Moderate head and tail winds decrease reach 10% to 15%.

SOLID STREAM NOZZLES

| Hand Lines | 50 psi nozzle pressure (GPM) | Master Streams | 80 psi nozzle pressure (GPM) |
| --- | --- | --- | --- |
| 1” | 200 | 1¼” | 400 |
| 1-1/8” | 250 | 1 3/8” | 500 |
| 1¼” | 300 | 1½” | 600 |
|  |  | 1 5/8” | 700 |
|  |  | 1¾” | 800 |
|  |  | 1 7/8” | 900 |
|  |  | 2” | 1000 |

ONE EIGHTH (1/8”) RULE:

1/8” change in nozzle diameter at 50 psi nozzle pressure changes the flow by approximately 50 GPM.

1/8” change in nozzle diameter at 80 psi nozzle pressure changes the flow by approximately 100 GPM up to and including 2” tips.

FRICTION LOSS FORMULAS FOR 100 FEET OF HOSE

| For 1½” Hose | FL = the FL in 2½” hose at 4 times the stated GPM |
| --- | --- |
| For 1¾” Hose | FL = (10 Q2) + 10 |
| For 2” Hose | FL = (2Q2 + Q) x 3 |
| For 2½ ” Hose | FL = (2Q2 +Q) |
| For 3” Hose | FL = (2Q2 +Q) x .4 |
| For 3½” Hose | FL =(2Q2+Q) x .17 |
| For 4” Hose | FL = (2Q2 +Q) x .1 |
| For 4½” Hose | FL =(2Q2 + Q) x .05 |
| For 5” Hose | FL = (2Q2 +Q) x .03 |

Example:      1½ ” hose flowing 100 GPM

x 4

2½ ” hose = 36 psi =  400 GPM

All of the above formulas give you the amount of friction loss per 100 feet of hose.

Q = GPM divided by 100.

Friction Loss 1½ ” Hose

To help simplify the computing of the Friction Loss in 1½” hose, the FAE Committee has accepted a standard GPM and Friction Loss commonly used in the fire service (100 GPM and 30 psi per 100 feet of hose).  This standard, 100 GPM and 30 PSI per 100 feet of hose will be used when teaching this course and for any testing requiring the computing of F.L. in 1½” hose.  The instructor may teach additional methods for computing F.L. in 1½” hose, but all FAE testing will only reflect the use of the above standard.

Friction Loss 1¾” Hose

To help simplify the computing of the Friction Loss in 1¾” hose, the FAE Committee has accepted a standard flow of 150 GPM and Friction Loss of 32 psi per 100 feet of 1¾ ” hose.  This standard, 150 GPM 32 psi per 100 feet of 1¾” hose will be used when teaching this course and for any testing requiring the computing of friction loss in 1¾” hose.  The instructor may teach additional methods for computing friction loss in 1¾” hose but all FAE testing will reflect the use of the above standard.

FIELD HYDRAULICS

250 GPM fog nozzle on a 2½” line = 15 lbs. per 100’ friction loss

100 GPM fog nozzle on a 1½” line = 30 lbs. per 100’ friction loss

150 GPM fog nozzle on a 1¾” line = 32 lbs. per 100’ friction loss

ELEVATION

Add  5 psi for each floor of elevation (exclude one floor)

Subtract 5 lbs. for each floor below grade

APPLIANCES

Add 25 psi for standpipe system and siamese

Add 10 psi for gated wyes and siamese

Add 20 psi for all master stream devices

Add 20 psi for in-line operations

SPRINKLER SYSTEMS

Sprinkler systems shall be maintained at 150 psi pump discharge pressures

Calculate flow from sprinkler heads by using the following formula:

Flow (in GPM’s) = ½ pressure (at sprinkler) + 15

HYDRANT RESIDUAL PRESSURE

A recommended minimum of 10 psi should be maintained on the compound gauge when taking water from a hydrant.

TRANSFER VALVE SETTINGS

Pump in CAPACITY when you are going to discharge over 50% of your pumpers capacity.  Pump in PRESSURE when you are going to have to develop a net pump pressure over 200 psi.

FRICTION LOSS

| 2½ Inch Rubber-lined Hose – Lbs. of Friction Loss per 100 feet |
| --- |
| 200 GPM | 200/100 = 2 | 2 x ( 2 x 2) + 2 = | 10 lbs. |
| 300 GPM | 300/100 = 3 | 2 x ( 3 x 3) + 2 = | 21 lbs. |
| 400 GPM | 400/100 = 4 | 2 x ( 4 x 4) + 2 = | 36 lbs. red line |
| 500 GPM | 500/100 = 5 | 2 x ( 5 x 5) + 2 = | 55 lbs. |
| 600 GPM | 600/100 = 6 | 2 x ( 6 x 6) + 2 = | 78 lbs. |
| 700 GPM | 700/100 = 7 | 2 x ( 7 x 7) + 2 = | 105 lbs. |
| 800 GPM | 800/100 = 8 | 2 x ( 8 x 8) + 2 = | 136 lbs. |
| 900 GPM | 900/100 = 9 | 2 x ( 9 x 9) + 2 = | 171 lbs. |
| 1000 GPM | 1000/100= 10 | 2 x (10 x 10) + 2 = | 210 lbs. |

| 3 Inch Hose - Lbs. of Friction Loss per 100 feet |
| --- |
| 200 GPM | 200/100 = 2 | 2 x 2 x 2 + 2 x .4 = | 4.0 lbs. |
| 300 GPM | 300/100 = 3 | 3 x 3 x 2 + 3 x .4 = | 8.4 lbs. |
| 400 GPM | 400/100 = 4 | 4 x 4 x 2 + 4 x .4 = | 14.4 lbs. |
| 500 GPM | 500/100 = 5 | 5 x 5 x 2 + 5 x .4 = | 22.0 lbs. |
| 600 GPM | 600/100 = 6 | 6 x 6 x 2 + 6 x .4 = | 31.2 lbs. red line |
| 700 GPM | 700/100 = 7 | 7 x 7 x 2 + 7 x .4 = | 42.0 lbs. |
| 800 GPM | 800/100 = 8 | 8 x 8 x 2 + 8 x .4 = | 54.4 lbs. |
| 900 GPM | 900/100 = 9 | 9 x 9 x 2 + 9 x .4 = | 68.4 lbs. |
| 1000 GPM | 1000/100= 10 | 10 x 10 x 2 + 10 x .4 = | 84.0 lbs. |

FRICTION LOSS

Red line friction loss - 36 lbs.  If friction loss goes over 36 lbs., a second line or larger diameter hose should be used.

|  | 3½ “ Hose | 4” Hose |
| --- | --- | --- |
|  | 2Q2 + Q x .17 = FL | 2Q2 + Q x .10 = FL |
| 200 GPM | 1.7 | 1.0 |
| 300 GPM | 3.5 | 2.1 |
| 400 GPM | 6.1 | 3.6 |
| 500 GPM | 9.3 | 5.5 |
| 600 GPM | 13.2 | 7.8 |
| 700 GPM | 17.8 | 10.5 |
| 800 GPM | 23.1 | 13.6 |
| 900 GPM | 29.0 | 17.1 |
| 1000 GPM | 35.7 | 21.0 |

|  | 4½ “ Hose | 5” Hose |
| --- | --- | --- |
|  | 2Q2 + Q x .05 = FL | 2Q2 + Q x .03 = FL |
| 200 GPM | 0.50 | 0.3 |
| 300 GPM | 1.05 | 0.6 |
| 400 GPM | 1.80 | 1.0 |
| 500 GPM | 2.70 | 1.6 |
| 600 GPM | 3.90 | 2.3 |
| 700 GPM | 5.20 | 3.1 |
| 800 GPM | 6.80 | 4.0 |
| 900 GPM | 8.50 | 5.1 |
| 1000 GPM | 10.50 | 6.3 |

SUMMARY

COURSE STANDARDS FOR CALCULATING ENGINE DISCHARGE PRESSURES

| Nozzles or Tips | Flows | Pressure Nozzle | Friction Loss/100” Hose |
| --- | --- | --- | --- |
|  |  |  | 1½” | 1¾” | 2½” | 3” |
| 1½” | 100 GPM | 100 psi | 30 |  |  |  |
| 1¾” | 150 GPM | 100 psi |  | 32 |  |  |
| 2½” | 250 GPM | 100 psi |  |  | 15 | 6 |
| 1” | 200 GPM | 50 psi |  |  | 10 | 4.0 |
| 1-1/8” | 250 GPM | 50 psi |  |  | 15 | 6.0 |
| 1¼” | 300 GPM | 50 psi |  |  | 21 | 8.4 |
| 1¼” | 400 GPM | 80 psi |  |  | *36* | 14.4 |
| 1-3/8” | 500 GPM | 80 psi |  |  | 55 | 22.0 |
| 1½” | 600 GPM | 80 psi |  |  | 78 | *31.2* |
| 1-5/8” | 700 GPM | 80 psi |  |  | 105 | 42.0 |
| 1¾” | 800 GPM | 80 psi |  |  | 136 | 54.4 |
| 1-7/8” | 900 GPM | 80 psi |  |  | 171 | 68.4 |
| 2” | 1000 GPM | 80 psi |  |  | 210 | 84.0 |

RED LINE:  **

FORMULA FOR ENGINE PRESSURE CALCULATIONS

DP = NP + FL + AFL + E

Pump discharge pressure =

Nozzle Pressure + Friction Loss + Appliance Friction Loss + Elevation

Relays = maintain 20 psi for receiving pumper

Hydrant Residual = maintain 10 psi from hydrant

Wyes/Siamese = 10 psi loss

Standpipe Systems = 25 psi loss

Master Stream Devices = 20 psi loss

Elevation = 5 psi/floor (exclude one floor) or ½ psi/foot

SUPPLY AND SUPPORT OF SPRINKLERS AND STANDPIPE SYSTEMS

The following are suggested methods to indicate if you’re not getting into a sprinkler or standpipe system with a supply line.

A.  In warm, humid weather, the lack of condensation on the hose coupling attached to the discharge port supplying this line.

B.  The discharge port and hose butt supplying this line is, or becomes, warm.

C.   Lack of a drop in the residual pressure as read on the compound gauge as this line is charged.  (Once the supply line is full, there is no further movement of water.)

D.  The inability to gate and feather various pressures on the discharge port to which this line is attached.  (The third principle of fluid pressure:  “ Pressure applied to a confined fluid from without, is transmitted in all directions without diminution.”)

NOTE:   Methods “A” and “B” may not be readily apparent, or the best indication, especially if the pumper is supplying additional lines which are already flowing.

FIRE SERVICE BASIC HYDRAULICS

Siamese Operations

When it becomes necessary for a pumper to deliver large quantities of water, a siamese operation will be needed.  Siamesing lines is one way of reducing the excessive friction loss created by large volume flows.  Though it may look difficult to compute, it is actually no harder than a single line.

When it becomes necessary to siamese, divide the GPM by the number of lines that pump is supplying.  Next, compute the friction loss for 1 line at the reduced GPM flow and disregard the other lines.   All that remains is to add either the Nozzle Pressure if supplying a deluge gun or 20 psi for residual pressure if supplying another engine.

EXAMPLE:  It is necessary to supply a deluge set with a 1¾” tip from 400’ away.  This lay would require 800 GPM which would create 55 lbs. F.L. per 100’ in 3” hose; therefore, siamesing is necessary.

EQUAL SIZE LINES

1.  Divide the total GPM by two lines.  This will give 400 GPM through each line.

2. Compute the friction loss for one line of 3” hose delivering 400 GPM:

4 x 4 x 2 + 4 = 36 x .4 = 14.4 or 15 lbs. F.L. per 100 ‘ of hose

3.  Multiply the F.L. for 100’ by length of the lay in hundreds of feet:

15 x 4 = 60 psi F.L. for the total lay

4.  To the 60 lbs. F.L., add 80 lbs. N.P. = 20 lbs. approximate loss for deluge set and this will be the engine discharge pressure:

60 + 80 + 20 = 160 lbs. engine pressure

Example:  If, in the above lay, it was necessary to use a 2½” and a 3” line, F.L. would be computed just a bit differently.

UNEQUAL SIZE LINES

1.  Divide the total GPM by two lines; this will give 400 GPM through each line

2.  Compute the friction loss for one line of 2½ ” hose delivering 400 GPM:

4 x 4 x 2 + 4 = 36 lbs. F.L. per 100’

3.  Compute the friction loss for one line of 3” hose delivering 400 GPM:

4 x 4 x 2 + 4 = 36 x .4 = 14.4 or 15 lbs. F.L. per 100’ of hose

4.  Add the Two F.L. answers together and divide by two:

36 + 15 = 51 : 2 = 25.5 lbs. F.L. per 100’ of hose

5.  Multiply the F.L. for 100’ by the length of the lay in hundreds of feet:

25 X 4 = 100 lbs. F.L. for the total lay

6.  To the 100 lbs. F. L., add 80 lbs. N.P. + 20 lbs. approximate F.L. in deluge set:

100 + 80 + 20 = 200 lbs. engine pressure

“RULE OF THUMB” for siamese of unequal size, but of equal length.  (2½” - 3”)

| 1”- 2½” and 1” - 3” Siamese lines |
| --- |
| Total GPM | F.L. – 100 ft. |
| 500 | 10 |
| 600 | 15 |
| 700 | 20 |
| 800 | 24 |
| 900 | 30 |
| 1000 | 40 |

FIRE SERVICE BASIC HYDRAULICS

Wye Operations

Wye operations are very common and are used, in one way or another, on just about any fire of consequence.  Sometimes they are used to get 1½” hand lines to the fire where the reach is too long for pre-connect.  On most large fires, they are used for overhaul from 2½” lines rather than laying longer and additional lines of 1½”.  Another use would be to get two 2½” lines on a fire from one 3” supply line.

Wye operations like siamese operations are used to reduce friction loss.  By the use of a wye, one may have one large supply line feeding two or more smaller hand lines.

Example:  400’ of 2½” hose wyed to two 200’ lines of 1 ½” hose.

1.  Total the GPM from both 1½” lines.  This is the amount of water for which the supply line must be computed.

100 GPM + 100 GPM = 200 GPM for both 1½” lines.

Therefore, the 2½” supply line is flowing 200 GPM.

2.  Compute the friction loss for the supply line.

2 x 2 x 2 + 2 = 10 lbs. F.L. for 100’

3.  Compute the friction loss for one 1½” line 200’ long.

30 lbs. F.L. per 100’ = 60 total  (disregard the second line)

4.         40 lbs. F.L. for 2½” supply line

+    60 lbs. F.L. for 1½” hand line

+  100 lbs. N.P.

+    10 lbs. for wye_______________

210 lbs. engine discharge pressure

The lay would give 200 GPM through two 1½” lines 600’ from the engine.  The engine would be running at a discharge pressure of 210 psi.

If there were two 1½” lines each 600’ in length, the discharge pressure would be 280 psi and the engine would be running at excessive RPM for the job.

FRICTION LOSS CALCULATIONS FOR ELEVATED STREAMS FROM PRE-PIPED WATERWAYS

When it is necessary to supply a pre-piped waterway, there are some basic facts that the FAE will have to know:

1.  It is necessary to supply the water to the pump inlets, or aerial intake when by-passing the pump and supplying the total operation.

2.  It is necessary to know the size tip that is intended for use in order to 	calculate pressure, determine the number of lines required and their 	diameter.

Since the waterways on pre-piped aerial are made of pipe, the following constants are used to determine the friction loss in the piping, master stream at different gallon flows.

The friction loss factor for pre-piped waterways will include the friction loss in the

- piping

- turret gun

- intake at the GPM flow provided

For course and testing purposes, the Fire Apparatus Engineer Committee has accepted a standard flow for pre-piped waterways of 1000 gpm.  When supplying a pre-piped waterway flowing a 1000 gpm, a friction loss of 60 psi will be used, which includes the intake, piping, and master stream device.  When pumping directly to the waterway, an additional 20 psi will be added for the friction loss in the direct piping.  Departments are encouraged to flow test their own apparatus to determine the actual friction loss.

There are 4 ways to supply a pre-piped waterway.

- Ladder truck pumps through internal piping to ladder.

- Ladder truck pumps through hose into the ladder intake.

- Engine company pumps into ladder intake.

- Relay to ladder truck pump operator (refer to relay operations).

Example 1:  It is necessary to supply a pre piped aerial ladder.  The aerial is elevated 50’ above grade on a 100’ aerial with a 2” tip (1000 gpm).  The FAE decides to use two 100’ lengths of 3” hose as feeder lines to supply the aerials siamese in the rear of the aerial.  Each of the lines will carry 500 gpm and the friction loss in the feeder lines will be about 22 lbs. For the 100’ lay.  The constant is 60 psi friction loss on a 100’ pre piped aerial ladder intake connection and master stream device.  Obtain the engine pressure and add as follows:

22 psi loss for two – 100’ lengths of 3” feeder line

60 psi loss for 100’ pre piped aerial, intake and master stream

25 psi loss for elevation

80 psi loss for nozzle pressure

187 psi will be the engine discharge pressure

Example 2:  Using the same pre piped aerial ladder as in Example 1, except this time the FAE will use the piping from the pump to the aerial.

60 psi loss for 100’ pre piped aerial, intake and master stream

20 psi loss for piping from the pump to the base of the aerial ladder

25 psi loss for elevation

80 psi for nozzle pressure

185 psi will be the engine discharge pressure

The examples given above have been figured with 60 psi. friction loss in the piping of a 100’ aerial ladder flowing 1000 gpm as a standard.

All students having aerial devices shall utilize the manufacturer’s specified friction loss in their department’s pre-piped aerials.

ELEVATED STREAM MISCELLANEOUS NOTES

The following are some recommended procedures for obtaining good elevated streams:

1.  Try to keep supply lines under 300 feet.

2.  Nozzle pressure should be 80 psi for solid streams and 100 psi for fog 	nozzles.

For each foot of elevation, the weight of water produces a pressure of .434 pounds per square inch.  This may be rounded off to 1/2 pound per foot of elevation for fire ground calculations.

Considering the simple basics, good elevated streams are possible if:

1.  The proper size tip or fog nozzle is used for the available water supply 	and pumping capacity.

2.  Sufficient lines of sufficient diameter are run from the pumper to the 	base of the elevated apparatus.

3.  Sufficient pressure is maintained.

The modern aerial ladder is a valuable piece of equipment of the department that uses it well.  Yet, if used incorrectly, firefighters can be seriously endangered; maintenance costs needlessly high; and fire losses increased.  Careful study, supervised training and constant practice are needed to bring the engineer’s skill to the highest point of efficiency.

GENERAL OPERATING SUGGESTIONS FOR CENTRIFUGAL FIRE PUMP

A centrifugal pump is designed for a specific duty and ordinarily will perform this duty satisfactorily over a long period of time.  On occasion, however, trouble will show up in one form or another and even an experienced operator may have difficulty in locating and correcting it.  The suggestions listed below should be helpful.

IF PUMP WILL NOT PRIME OR LOSES PRIME

A.  Air Leaks

1.  Faulty Connection

a.  suction hose or gasket

b.  discharge valves or gaskets

c.  booster tank

d.  drain valves

e.  gauge

2.  Faulty pump packing

3.  Leaky pump gaskets

All suction hose gaskets should be wiped clean of sand, pebbles, and any other foreign matter before hose is attached to the pump.  Hose couplings should be tightened snugly enough to make air-tight connections.  Main pump packing should always be kept adjusted tightly enough to prevent excessive leakage (see manufacturer’s operating instructions for proper packing adjustment procedure).

B.    Detecting Air Leaks

1.  Connect suction hose to the pump with a cap on the opposite end of the hose.

2.  Close all pump openings

3.  Opening the priming valve and operate the primer until a vacuum of from 20-22 inches of mercury is shown on the vacuum gauge. (If impossible to draw this much vacuum, primer may be defective.

4.  Close the priming valve and shut off the primer.  Shut off the engine.

a.  If leaks are present, the vacuum will promptly decrease as shown by the vacuum gauge.

b.  If the vacuum drops more than 10 inches of mercury in five minutes.

C.  Locating Air Leaks

Air leaks may frequently be detected by ear if the engine is stopped.  Applying water or oil to the suspected points may aid in detecting leaks.  Leaks may be found by applying water pressure to the pump and suction hose by means of an auxiliary pump or hydrant.  Pressures should be approximately 50 psi and should not exceed that recommended for the suction hose or pump.

1.  Dirt in Suction Screens

Dirt clogged suction screens may make it difficult to prime the pump, as well as cause the pump to lose its prime after it is started.  When operating from draft, be sure suction screens are kept clean.  Be sure to keep the end of the suction hose off the lake or river bottom.  For this purpose, a special box or basket, which fits around the suction strainer or is threaded to the end of the hose, is frequently fabricated.

2.  Engine Speed Too Low

Follow the manufacturer’s recommendation for priming.   Speeds higher than those recommended do not accelerate priming.

3.  Primer Not Operated Long Enough

Follow manufacturer’s recommendation.  The maximum time for priming for lifts to ten feet should not exceed 30 seconds for 1250 GPM pumps or below, or 45 seconds for 1500 GPM pumps or above.

4.  Lack of Oil Primer Reservoir

Where a mechanically driven or electrically driven rotary primer is in use, an adequate supply of oil should always be kept in the reservoir to lubricate and “seal” the priming pump.

5.  Improper Clearance in Rotary Primer

Due to wear, the clearance between the priming pump rotors and head may become so large as to cause poor priming characteristics.  In this case, the proper clearance should be restored by the method outlined by the manufacturer in the priming pump operating instructions.

6.  Excess Carbon on Exhaust Primer Valve Seats

See exhaust primer manufacturer’s operating instructions for methods to remove carbon.

7.  Defective Priming Valve

A broken or deteriorated priming valve spring may cause the valve to leak and the pump to lose its prime.  Worn parts in the priming valve may also allow air leakage.

8.  High Point in Suction Line

High points in the suction line (caused, for example, by running suction hose over a bridge railing) create air pockets which may cause loss of prime.  In some cases, it may be impossible to rearrange the suction hose to eliminate the high point.  In this case, prime may be obtained by closing the discharge valve 	immediately when the pressure drops and then repriming.  This procedure 	usually eliminates the air pocket which was drawn into the impellers when the pump was started after first priming; however, it may have to be repeated in some situations.

9.  Suction Lift Too High

Lifts of more than 20 feet should not be attempted, even at low altitudes, unless there are practically no air leaks and the equipment is in new condition.  In this case, higher lifts may be obtained.

10.  End of Suction Hose Not Under Water

The end of the hose may be submerged deeply enough for priming, but when a large volume of water is pumped, a whirlpool is sometimes formed which uncovers the end of the hose.

AUTOMATIC PUMP PRESSURE CONTROLLER

The automatic pump pressure controller is a device which regulates engine speed of a pumper to preclude surges or drops in the pressure of operating discharge lines as other lines are closed or opened.

The basic method by which the device works is to compare the pump discharge pressure to a reference pressure stored, when the pump is set into operation, in a device called an accumulator.  As pump discharge pressure varies in response to changing discharge volumes, the reference pressure in the accumulator acts on a hydraulic cylinder which in turn actuates a rod connected to the throttle linkage thereby adjusting engine speed.

The operating range of most automatic pump pressure controllers is between 75-500 pounds.  If pump pressure drops below 30 pounds per square inch, the unit automatically disengages,  thus protecting the engine as in the case of loss of prime.  This device is equally effective with gasoline or diesel engines.

IF PUMP WILL NOT DELIVER CAPACITY

The following may prevent the pump from delivering its rated capacity.

1.  Relief Valve Improperly Set

If a relief valve is set at a pressure below the desire operating pressure, it will by pass water and lower the capacity (see manufacturer’s relief valve operating instructions).

2.  Badly Worn Wear Rings

Failure of the pump to deliver its rated capacity at a given pressure may be an indication that the impeller wear rings are badly worn, allowing excessive quantities of water to leak around them.

3.  Suction Screen and Impeller Vanes Fouled with Debris

Backwash of water from the pump through the impellers when the pump is stopped usually cleans the impeller vanes.  Debris on the pump suction screen, however, usually remains in the suction hose and is immediately caught by the screen when pumping is resumed.  Therefore, suction hose should be removed and cleaned.

4.  Chassis Transmission in Wrong Gear

See operating instructions.

5.  Suction Hose Collapsed

On defective or old suction hoses, the inner liner often collapses when drafting water, thus restricting the flow of water to the pump.  Collapse of the inner liner is often hard to detect even when the inside of the hose is examined with a light. This is due to the fact that the inner liner often goes back in place when the suction vacuum is removed. If the pump will deliver capacity with a different suction hose, it is reasonable to assume that the liner on the former hose has become loosened.

6.  Suction Hose Not Submerged Deeply Enough

The lower end of the suction hose should be submerged at least two feet below 	the surface of the water to avoid taking air.

7.  Suction Hose Too Small

When higher than normal lifts are involved or at high altitudes, larger suction hose is needed.

8.  Insufficient Engine Power

Although the engine had sufficient power originally, there are several reasons why the power can decrease to the point at which it will not handle the pump at the rated capacity and pressure. Things to suspect are:  incorrect timing, fouled spark plugs, burned distributor points, weak condenser or coil, sticking valves, worn piston rings, worn fuel pump, and poor carbonation.  Also, if the engine is operated at higher than normal altitudes, the power may be too low.  The power of an engine decreases about 3% to 4% for every 1000 feet of increase in altitude. Excessive engine temperatures, which frequently occur in hot weather, and during long periods of operation, reduce the power.  This can be caused by clogged radiator or heat exchanger, insufficient coolant, worn water pump, loose fan belt, and deteriorated crank case oil.

9.  Transfer Valve Improperly Set (does not apply to single stage pumps)

The valve should be in “parallel” (volume) position when pumping more than one-half rated capacity.  When changing the position of the valve, make sure it is moved completely into the new position; if not, pump performance may be seriously affected.

IF PUMP WILL NOT DEVELOP SUFFICIENT PRESSURE

In general, there should be conditions which prevent the pump from delivering rated capacity will also affect the pressure adversely.  The following may prevent the pump from developing sufficient pressure:

1.  Relief Valve Improperly Set

A relief valve properly set will prevent the pump pressure from rising much above 	that at 	which it is set; consequently, too low a setting causes too low a pressure. (See manufacturer’s relief valve operating instructions).

2.  Insufficient Pump Speed

Insufficient pump speed may be due to one or more of the following causes:

a.  impeller wear rings or other pump parts binding

b.  clutch slipping

c.  chassis transmission in wrong gear

d.  governor limiting engine speed

e.  insufficient engine power

3.  Transfer Valve Improperly Set (does not apply to single stage pumps)

The transfer valve should be in “series” (pressure) position when pumping at high pressures.

4.  Capacity Limiting Pressure

Care should be taken not to attempt to take more water from the pump than it can handle at the desired pressure (see instructions on operation of pump).  If the pump is operating at draft under normal suction conditions and the maximum rated capacity is exceeded, the pressure will be low due to the characteristic of a centrifugal pump even if the engine has plenty of power and speed.  Also, excess capacity may raise the suction vacuum to a point above that which the pump was designed and lowered pressures will result.  On pumping units having engines with low surplus power, the pressure will be limited by engine power if surplus capacity is being pumped.

SUPPLYING A STANDPIPE SYSTEM WHEN THE FIRE DEPARTMENT CONNECTION IS NOT USABLE

When the fire department connection (siamese) supporting a standpipe system is not useable; and, where the check valve below the fire department connection (siamese) is inoperative, the following procedure should be followed:

1.  Stretch a line from the pumper to a gated outlet on the first floor.

2.  Remove any house lines, reducer connections, and/or pressure reducers.

3.  Connect the pumper supply line to the discharge outlet using a double female adapter.

4.  When water is started in the supply line, the outlet valve is opened fully to allow water to flow into the riser.

5.  Where the hose outlet extends at a right angle from the riser, the weight of the hose and fittings should be supported by a short length of rope.

6.  If necessary, additional lines can be similarly stretched to hose outlets on other floors.

When the fire department connection (siamese) has a frozen swivel, placing a double male and double female on the connection can overcome this difficulty.